## Description

The SP-1CAN is a combined alarm, monitoring and discharge panel used for controlling Pyrogen MAG generators and any type of initiators.

When connected to, it can monitor for faults as well as alarm information from a number of different types of detectors, including linear heat sensing cable or spot detectors of potential free type, which could be smoke (optical/ionisation), heat, IR-flame, water or gas.

The status information will be presented on the vehicle LCD monitor by interfaceing with the vehicle CAN bus communication system.

At the rear of the panel there are a number of terminals to allow the user to connect to the CAN bus system, external sounders, warning beacons, relay connections for automatic engine shutdown in event of fire as well as an external manual discharge button should this be required. All cables, whether they are for the detectors, warning devices, power supply or for

the MAG generators are connected at the rear of the panel.

The SP-1CAN is an extremely compact control panel allowing adaptability to most standard instrument modules (VDO instruments).

The panel is both robust, water & dust resistant up to IP 65 and is delivered ready for purpose and set to operate in a Manual mode, (factory default).

However by careful alteration of the DIP switches on the back of the panel it can be programmed to operate in an automatic mode, which after receiving a signal from one of the detectors or sensors indicating the existence of a fire, will activate the MAG units remotely after a preset 15 second delay.

All inputs will be monitored continuously assuming that the panel remains connected to the power supply. Should a short or open circuit signal be detected it will result in a “Fault” indication.

## Technical specifications

Technical Specification SP-1-CAN

Power Supply

| Operating voltage | 8 - 28 VDC |
| --- | --- |
| Standby current (8 – 28 VDC) | 2 mA (ignition off) |
| Normal current | 50 mA |
| Internal automatic fuse | 2 A |
| Fuse on supply lead | 3 A |

# Auto/Man Input & Sleep Function

| From ignition- or main switch | + 8 to 28 VDC (2 mA) |
| --- | --- |

## Alarm loop 1 (NO switch)

| Alarm Temperature | 105°C |
| --- | --- |
| Maximum normal ambient temp | 75°C |
| Voltage | 3 VDC |
| Normal current/Alarm current | 0.03 / 0.06 mA |
| Sensor cable EOL resistor | 47kΩ |

## Alarm loop 2 (NC switch)

| Alarm situation, resistor value on loop | 47kΩ |
| --- | --- |
| Normal situation, resistor value on loop | 23,5kΩ |
| EOL resistors on NC alarm contact | 2x47kΩ |
| Voltage | 3 VDC |
| Normal current/Alarm current | 0.03/ 0.12 mA |

## Remote manual discharge loop

| Alarm situation, resistor value on loop | 47kΩ |
| --- | --- |
| Normal situation, resistor value on loop | 23,5kΩ |
| EOL resistors on NC alarm contact | 2x47kΩ |
| Voltage | 3 VDC |
| Normal current/Alarm current | 0.03/ 0.12 mA |

## Discharge Signal

| Duration (Pulse time) | 10 sec |
| --- | --- |
| Voltage | 8 - 28 VDC |
| Discharge current (Max) | 1,2 A (current limitation) |
| Normal current 12V/24V | 0.25 / 0.5 mA |
| Max number of MAG generators | 2 (12 V dc) or 4 (24 V dc) |

## Alarm/Fault output (Output 1)

| Voltage | 8 - 28 V dc |
| --- | --- |
| Current (max) | 1.8 A |

## Activated (Output 2)

| Voltage | 8 - 28 V dc |
| --- | --- |
| Current (max) | 1.8 A |

## CAN Bus (Controller Area Network) Interface

| Communication | CAN 2.0B |
| --- | --- |
| Protocol | Supports most protocols |

# Text boxes

# PyroSense SP-1CAN  Control Device

## Features

- 1 monitored Pyrogen MAG Output (2 or 4 MAG units)

- 2 monitored detector alarm loop inputs

- 1 monitored external discharge alarm input

- Ignition “panel switch on”

- Power 8–28 V DC

- Internal alarm/fault buzzer

- Engine & ventilation shut down output

- General fault, alarm & discharged output

- Press button for silencing of audible

- Press button for resetting of the panel

- Press buttons simultaneously for discharge of Pyrogen

- Dual LED indicators for power ok, general fault, alarm and discharged.

- CAN Bus interface for communication with vehicle information system

PRESS

## Fire Control

PRESS

Reset

IN THE EVENT

OF FIRE

Press both buttons

for 5 sec.

Silence

Alarm

Activated

Fault

Power

Pyrogen Ltd.

Gilnow Mill Business Centre

Spa Road,

Bolton U.K.

BL1 4LF

Tele: 	+44 (0) 1204 373300

Fax:	+44 (0) 1204 373355

e.mail	pyrogen@btconnect.com

www.pyrogen.com

15

16

DIP-switches

14

13

12

11

10

9

# OFF

80- 00 OCLA N O

6 5 4 3 2 1

8

7

6

5

4

3

2

1

IN THE EVENT

OF FIRE

PRESS

Fire Control

PRESS

Press both buttons

for 5 sec.

Reset

Silence

Activated

Alarm

Fault

Power